## Worksheet
Instructions:
1) Edit the PEACH colored cells. 2) Use Pull-Downs for RadType/MAIN & Pipe Size. 3) Click "Recommendation" Tab for results.
Recommended resource: E.D.R. by Dan Holohan available for purchase www.heatinghelp.com
Formulas and Data based on: Balancing Steam Systems by Gerry Gill & Steve Pajek available for purchase www.heatinghelp.com
Developed by: JP Freeley - Nov 2009 - jpf321@gmail.com
ElementName	sq ft EDR	BTUH (240BTUH X SqFtEDR)	RadType	RadCF to Vent	Pipe Size	runout length (ft)	total CF (Rad+Pipe)	Minutes To Vent	CFM to Vent
MAIN Example 1	0	0	Main	0.000	2"	65	1.495	3	0.498
MAIN Example 2	0	0	Main	0.000	2"	55	1.265	3	0.422
Rad Example 1st Flr	24.5	5880	Cast-iron tube (circa 1930)	0.319	1-1/4"	1	0.329	7	0.047
Rad Example 2nd Flr	52.5	12600	Cast-iron tube (circa 1930)	0.683	1-1/4"	10	0.783	5	0.157
Rad Example 3rd Flr	21	5040	Cast-iron tube (circa 1930)	0.273	1-1/4"	20	0.473	3	0.158
	0	0	Cast-iron tube (circa 1930)	0.000	1-1/4"	0	0.000	5	0.000
	0	0	Cast-iron tube (circa 1930)	0.000	1-1/4"	0	0.000	5	0.000
	0	0	Cast-iron radiant radiator (5" deep)	0.000	1-1/4"	0	0.000	3	0.000
	0	0	Cast-iron tube (circa 1930)	0.000	1-1/4"	0	0.000	7	0.000
	0	0	Cast-iron tube (circa 1930)	0.000	1-1/4"	0	0.000	7	0.000
	0	0	Cast-iron tube (circa 1930)	0.000	1-1/4"	0	0.000	7	0.000
	0	0	Cast-iron tube (circa 1930)	0.000	1-1/4"	0	0.000	5	0.000
	0	0	Cast-iron tube (circa 1930)	0.000	1-1/4"	0	0.000	5	0.000
	0	0	Cast-iron tube (circa 1930)	0.000	1-1/4"	0	0.000	5	0.000
	0	0	Cast-iron radiant radiator (5" deep)	0.000	1-1/4"	0	0.000	3	0.000
	0	0	Cast-iron radiant radiator (5" deep)	0.000	1-1/4"	0	0.000	3	0.000
TOTAL	98	23520					1.281

## Recommendations Gorton
Gorton Valve Options					Element	1oz	Cap	2oz	Cap	3oz	Cap
#4, #5, #6, #C and #D available as 1/8" Angles					MAIN Example 1	0pcs #2s & 2pcs #1s	0.660	0pcs #2s & 1pcs #1s	0.540	0pcs #2s & 1pcs #1s	0.700
#4, #5, #6, #C and #D available as 1/4" or 1/8" Straight					MAIN Example 2	0pcs #2s & 2pcs #1s	0.660	0pcs #2s & 1pcs #1s	0.540	0pcs #2s & 1pcs #1s	0.700
#1 available as 3/8"M, 3/4"M or 1/2"F Straight					Rad Example 1st Flr	#5	0.080	#5	0.130	#4	0.055
#2 available as 1/2"M Straight					Rad Example 2nd Flr	#C	0.270	#6	0.235	#5	0.160
					Rad Example 3rd Flr	#C	0.270	#6	0.235	#5	0.160
Main Venting Manifold Size					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
1/2" pipe can support 2pcs #2					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
3/4" pipe can support 4pcs #2 + 1pcs #1					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
1" pipe can support 5pcs #2					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
Main Vent Conversions					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
~4pcs Gorton #1 = 1pc Gorton #2					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
~2pcs Hoffman #75 = 1pc Gorton #2					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
~3pcs Hoffman #76 = 1pc Gorton #2					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
						Total Vent Capacity (cfm)	1.940		1.680		1.775
						Venting Needed (cfm)	1.28		1.28		1.28
						Venting Surplus (cfm)	0.659		0.399		0.494
						Venting Surplus (%)	51%		31%		39%

## Recommendations Hoffman1A
Hoffman 1A Valves					Element	1oz	Cap	2oz	Cap	3oz	Cap
Are fully adjustable from 1-6 and available as 1/8" Angles					MAIN Example 1	0pcs #2s & 2pcs #1s (Gorton)	0.660	0pcs #2s & 2pcs #1s (Gorton)	0.540	0pcs #2s & 2pcs #1s (Gorton)	0.700
					MAIN Example 2	0pcs #2s & 2pcs #1s (Gorton)	0.660	0pcs #2s & 2pcs #1s (Gorton)	0.540	0pcs #2s & 2pcs #1s (Gorton)	0.700
					Rad Example 1st Flr	3	0.100	3	0.158	2	0.056
					Rad Example 2nd Flr	6	0.145	3	0.158	3	0.200
					Rad Example 3rd Flr	6	0.145	3	0.158	3	0.200
Main Venting Manifold Size					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
1/2" pipe can support 2pcs #2 (Gorton)					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
3/4" pipe can support 4pcs #2 + 1pcs #1 (Gorton)					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
1" pipe can support 5pcs #2 (Gorton)					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
MAIN VENTS ARE PROVIDED AS GORTON BRAND					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
					0	#N/A	0.000	#N/A	0.000	#N/A	0.000
						Total Vent Capacity (cfm)	1.710		1.554		1.856
						Venting Needed (cfm)	1.28		1.28		1.28
						Venting Surplus (cfm)	0.429		0.273		0.575
						Venting Surplus (%)	33%		21%		45%

## Tables (Gill & Pajek)
				Hidden Columns A-R containing data tables
				Gorton Capacities
Radiator Type	CF/sqftEDR		Pipe Size	CFM/PipeLinFoot			1oz	2oz	3oz			Hoffman 1A Capacities
Main	0.0000		1-1/4"	0.010		#1	0.330	0.540	0.700			1oz	2oz	3oz
Unit heater	0.0002		1-1/2"	0.014		#2	1.100	1.750	2.200		1	0.020	0.026	0.033
Cast-iron convector (in cabinet)	0.0003		2"	0.023		#4	0.025	0.040	0.055		2	0.026	0.043	0.056
Cast-iron thin tube (as made today)	0.0090		2-1/2"	0.030		#5	0.080	0.130	0.160		3	0.100	0.158	0.200
Cast-iron baseboard (10"-high)	0.0100		3"	0.053		#6	0.150	0.235	0.300		4	0.108	0.160	0.210
Cast-iron tube (circa 1930)	0.0130		3-1/2"	0.070		#C	0.270	0.450	0.570		5	0.140	0.220	0.290
Cast-iron column (circa 1900)	0.0250		4"	0.090		#D	0.330	0.540	0.700		6	0.145	0.225	0.300
Cast-iron wall- or ceiling-mounted	0.0280		4-1/2"	0.110
Cast-iron flue (antique radiators)	0.0290		5"	0.140
Cast-iron radiant radiator (5" deep)	0.0090		6"	0.200
			8"	0.360
CFM_Vent_Lookup_1oz					CFM_Vent_Lookup_3oz			CFM_Vent_Lookup_Hoff1A_1oz			CFM_Vent_Lookup_Hoff1A_2oz			CFM_Vent_Lookup_Hoff1A_3oz
CFM_Max	gorton		CFM_Vent_Lookup_2oz			CFM_Max	gorton		CFM_Mac	Hoff1a		CFM_Mac	Hoff1a		CFM_Mac	Hoff1a
0	#4		CFM_Max	gorton		0	#4		0	1		0	1		0	1
0.03	#5		0	#4		0.06	#5		0.02	2		0.03	2		0.03	2
0.08	#6		0.04	#5		0.16	#6		0.03	3		0.04	3		0.06	3
0.15	#C		0.13	#6		0.3	#C		0.1	4		0.16	4		0.2	4
0.27	#D (#1 if Main Vent)		0.24	#C		0.57	#D (#1 if Main Vent)		0.11	5		0.16	5		0.21	5
			0.45	#D (#1 if Main Vent)					0.14	6		0.22	6		0.29	6

			Main_Vent_LU		#2
				#1	1.1
			1oz	0.33	1.75
			2oz	0.54	2.2
			3oz	0.7